## LF minimum input
BLOR Excel load flow report tool Type B PGM revision 01-01-2025 |  |  |  |  | Results loadflow | Pmax | Cases 1 - 13 | [12 empty] | Points 3-4
[5 empty] | Cases Q-U resp. Q-P (NBNL RFG CVD v1.3 | P (Qc=0) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | P3 | P4
[5 empty] | Uc grid voltage (p.u.) | 1 | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.05 | 0.95 | 0.95 | 0.9 | 0.9 | 0.85 | 1 | 1
[5 empty] | Active power connection point Pc (MW) | 10.013 | 9.931 | 9.852 | 2 | 2 | -0.007 | 9.973 | 9.984 | 9.864 | 9.352 | 9.153 | 9.354 | 9.352 | 8.304 | 4.96 | 4.92
Name PGM | Name as per PGMD |  |  |  | Reactive power connection point Qc (Mvar) | -0.002 | -3.295 | 3.313 | -3.29 | 3.309 | -0.002 | -3.34 | 0.002 | 3.32 | 3.308 | -3.31 | 2.5 | 0 | 3.11 | -3.3 | 3.31
Grid | Declared voltage connection point Uc (kV): | 10.5 |  |  | Active power connection point Pc (p.u) | 1 | 0.99181 | 0.98392 | 0.19974 | 0.19974 | -0.00069909 | 0.99601 | 0.9971 | 0.98512 | 0.93399 | 0.91411 | 0.93419 | 0.93399 | 0.82932 | 0.49536 | 0.49136
| Maximum active power PGM Pmax at Qc=0 (MW) | 10.013 |  |  | Reactive power connection point Qc (p.u.) | -0.00019974 | -0.32907 | 0.33087 | -0.32857 | 0.33047 | -0.00019974 | -0.33357 | 0.00019974 | 0.33157 | 0.33037 | -0.33057 | 0.24968 | 0 | 0.3106 | -0.32957 | 0.33057
| Connection capacity grid connection point (MVA) | 10 |  |  | Apparent power connection point (MVA) | 10.013 | 10.4634 | 10.3941 | 3.8502 | 3.8665 | 0.0072801 | 10.5174 | 9.984 | 10.4077 | 9.9198 | 9.7331 | 9.6823 | 9.352 | 8.8673 | 5.9575 | 5.9298
Unit 1 type: | wind turbine or PV-inverter |  |  |  | Unit type 1 | P (Qc=0) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 3 | 4
Unit 2 type: | wind turbine or PV-inverter |  |  |  | Maximum apparent power unit (kVA) | 203 | 209 | 215 | 76 | 79 | 0 | 210 | 202 | 215 | 206 | 193 | 190 | 197 | 185 | 209 | 215
Unit 3 type | wind turbine or PV-inverter |  |  |  | Maximum voltage unit (V) | 798.4 | 782.4 | 814.4 | 768.8 | 800.8 | 781.6 | 860 | 874.4 | 852 | 776 | 731.2 | 721.6 | 742.4 | 698.4 | 782 | 814
| Unit type | 1 | 2 | 3 | Minimum voltage unit (V) | 789.6 | 774.4 | 803.2 | 768 | 797.6 | 781.6 | 852.8 | 866.4 | 841.6 | 764.8 | 720.8 | 711.2 | 735.2 | 688 | 774 | 803
Unit data | Total number | 50 | 50 | 50 | Maximum current unit (A) | 148.4323 | 155.819 | 154.5447 | 57.1336 | 57.1849 | 0 | 142.1711 | 134.6084 | 147.4932 | 155.5101 | 154.5902 | 154.2415 | 154.7035 | 155.2468 | 155.8995 | 154.5832
| Apparent power Snom (kVA) | 215 | 215 | 215 | Maximum apparent power unit (p.u.) | 0.94419 | 0.97209 | 1 | 0.35349 | 0.36744 | 0 | 0.97674 | 0.93953 | 1 | 0.95814 | 0.89767 | 0.88372 | 0.91628 | 0.86047 | 0.97209 | 1
| Active power Pnom (kW) | 200 | 200 | 200 | Maximum voltage unit (p.u.) | 0.998 | 0.978 | 1.018 | 0.961 | 1.001 | 0.977 | 1.075 | 1.093 | 1.065 | 0.97 | 0.914 | 0.902 | 0.928 | 0.873 | 0.9775 | 1.0175
| Maximum reactive power supply +Qnom (kVAr) | 100 | 100 | 100 | Minimum voltage unit (p.u.) | 0.987 | 0.968 | 1.004 | 0.96 | 0.997 | 0.977 | 1.066 | 1.083 | 1.052 | 0.956 | 0.901 | 0.889 | 0.919 | 0.86 | 0.9675 | 1.0037
| Maximum reactive power absorption -Qnom (kVAr) | -100 | -100 | -100 | Maximum current unit (p.u.) | 0.95639 | 1.004 | 0.99578 | 0.36813 | 0.36846 | 0 | 0.91605 | 0.86732 | 0.95034 | 1.002 | 0.99607 | 0.99382 | 0.9968 | 1.0003 | 1.0045 | 0.99603
| Nominal voltage Unom (V) | 800 | 800 | 800 | Maximum voltage limit unit (p.u.) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
| Maximum current Imax (A) | 155.2 | 155.2 | 155.2 | Minimum voltage limit unit (p.u.) | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
| Maximum voltage Umax (V) | 880 | 880 | 880 | Unit type 2 | P (Qc=0) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 3 | 4
| Minimum voltage Umin (V) | 680 | 680 | 680 | Maximum apparent power unit (kVA) | 203 | 209 | 215 | 76 | 79 | 0 | 210 | 202 | 215 | 206 | 193 | 190 | 197 | 185 | 209 | 215
[5 empty] | Maximum voltage unit (V) | 798.4 | 782.4 | 814.4 | 768.8 | 800.8 | 781.6 | 860 | 874.4 | 852 | 776 | 731.2 | 721.6 | 742.4 | 698.4 | 782 | 814
[5 empty] | Minimum voltage unit (V) | 789.6 | 774.4 | 803.2 | 768 | 797.6 | 781.6 | 852.8 | 866.4 | 841.6 | 764.8 | 720.8 | 711.2 | 735.2 | 688 | 774 | 803
[5 empty] | Maximum current unit (A) | 148.4323 | 155.819 | 154.5447 | 57.1336 | 57.1849 | 0 | 142.1711 | 134.6084 | 147.4932 | 155.5101 | 154.5902 | 154.2415 | 154.7035 | 155.2468 | 155.8995 | 154.5832
[5 empty] | Maximum apparent power unit (p.u.) | 0.94419 | 0.97209 | 1 | 0.35349 | 0.36744 | 0 | 0.97674 | 0.93953 | 1 | 0.95814 | 0.89767 | 0.88372 | 0.91628 | 0.86047 | 0.97209 | 1
[5 empty] | Maximum voltage unit (p.u.) | 0.998 | 0.978 | 1.018 | 0.961 | 1.001 | 0.977 | 1.075 | 1.093 | 1.065 | 0.97 | 0.914 | 0.902 | 0.928 | 0.873 | 0.9775 | 1.0175
[5 empty] | Minimum voltage unit (p.u.) | 0.987 | 0.968 | 1.004 | 0.96 | 0.997 | 0.977 | 1.066 | 1.083 | 1.052 | 0.956 | 0.901 | 0.889 | 0.919 | 0.86 | 0.9675 | 1.0037
[5 empty] | Maximum current unit (p.u.) | 0.95639 | 1.004 | 0.99578 | 0.36813 | 0.36846 | 0 | 0.91605 | 0.86732 | 0.95034 | 1.002 | 0.99607 | 0.99382 | 0.9968 | 1.0003 | 1.0045 | 0.99603
[5 empty] | Maximum voltage limit unit (p.u.) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
[5 empty] | Minimum voltage limit unit (p.u.) | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | Unit type 3 | P (Qc=0) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 3 | 4
[5 empty] | Maximum apparent power unit (kVA) | 203 | 209 | 215 | 76 | 79 | 0 | 210 | 202 | 215 | 206 | 193 | 190 | 197 | 185 | 209 | 215
[5 empty] | Maximum voltage unit (V) | 798.4 | 782.4 | 814.4 | 768.8 | 800.8 | 781.6 | 860 | 874.4 | 852 | 776 | 731.2 | 721.6 | 742.4 | 698.4 | 782 | 814
[5 empty] | Minimum voltage unit (V) | 789.6 | 774.4 | 803.2 | 768 | 797.6 | 781.6 | 852.8 | 866.4 | 841.6 | 764.8 | 720.8 | 711.2 | 735.2 | 688 | 774 | 803
[5 empty] | Maximum current unit (A) | 148.4323 | 155.819 | 154.5447 | 57.1336 | 57.1849 | 0 | 142.1711 | 134.6084 | 147.4932 | 155.5101 | 154.5902 | 154.2415 | 154.7035 | 155.2468 | 155.8995 | 154.5832
[5 empty] | Maximum apparent power unit (p.u.) | 0.94419 | 0.97209 | 1 | 0.35349 | 0.36744 | 0 | 0.97674 | 0.93953 | 1 | 0.95814 | 0.89767 | 0.88372 | 0.91628 | 0.86047 | 0.97209 | 1
[5 empty] | Maximum voltage unit (p.u.) | 0.998 | 0.978 | 1.018 | 0.961 | 1.001 | 0.977 | 1.075 | 1.093 | 1.065 | 0.97 | 0.914 | 0.902 | 0.928 | 0.873 | 0.9775 | 1.0175
[5 empty] | Minimum voltage unit (p.u.) | 0.987 | 0.968 | 1.004 | 0.96 | 0.997 | 0.977 | 1.066 | 1.083 | 1.052 | 0.956 | 0.901 | 0.889 | 0.919 | 0.86 | 0.9675 | 1.0037
[5 empty] | Maximum current unit (p.u.) | 0.95639 | 1.004 | 0.99578 | 0.36813 | 0.36846 | 0 | 0.91605 | 0.86732 | 0.95034 | 1.002 | 0.99607 | 0.99382 | 0.9968 | 1.0003 | 1.0045 | 0.99603
[5 empty] | Maximum voltage limit unit (p.u.) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
[5 empty] | Minimum voltage limit unit (p.u.) | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | Cell Color identification | 2: Cells for input data and results load flow calculations
Reminder: calculated value exceeds connection capacity
Calculated values, parameter within targets, capability, not exceeding limits
Calculated values, parameter outside targets, capability, exceeding limits
Calculated or copied values for information
Explanation using BLOR report tool see memo
Click on DNV document below | [5 empty] | P (Qc=0): Grid code Q-U window at connection point
Right click mouse |  |  |  |  | Uc (p.u.) | P (Qc=0): 0.9; 1: 0.95; 2: 1.05; 3: 1.1; 4: 1.1; 5: 0.95; 6: 0.9; 7: 0.9
Unprotect Macro protection if applicable |  |  |  |  | Pmax (MW) at Qc=0: | P (Qc=0): 10.013; 1: 10.013; 2: 10.013; 3: 10.013; 4: 10.013; 5: 10.013; 6: 10.013; 7: 10.013
Choose "Acrobat Document Object" and "Open" |  |  |  |  | Q/Pmax, Qc=0 | P (Qc=0): 0.2; 1: 0.33; 2: 0.33; 3: 0; 4: -0.33; 5: -0.33; 6: 0; 7: 0.2
Memo should open in Acrobat window |  |  |  |  | Qmax | P (Qc=0): 2.0026; 1: 3.3043; 2: 3.3043; 3: 0; 4: -3.3043; 5: -3.3043; 6: 0; 7: 2.0026
Or download BLOR report tool explanation from
Eisen voor opwekeenheden, opslag, verbruikseenheden met vraagsturing en HVDC ¦ Netbeheer Nederland | [5 empty] | P (Qc=0): Grid code Q-P window at connection point
[5 empty] | Pmax (MW) at Qc=0: | P (Qc=0): 10.013; 1: 9.3121; 2: 2.0026; 3: 0; 4: 2.0026; 5: 9.3121; 6: 10.013
[5 empty] | Q/Pmax, Qc=0 | P (Qc=0): 0; 1: 0.33; 2: 0.33; 3: 0; 4: -0.33; 5: -0.33; 6: 0
[5 empty] | Qmax | P (Qc=0): 0; 1: 3.3043; 2: 3.3043; 3: 0; 4: -3.3043; 5: -3.3043; 6: 0
9
Note on I1: Berekening op basis van EN50549-2 hoekpunten bij maximaal vermogen
Note on H3: Fixed per unit voltage at connection point as required for load flow case
Note on H4: MW at connection point of PPM in load flow case
Note on C5: Name of PPM as per PGMD form
Note on H5: Mvar at connection point of PPM in load flow case
Note on D6: Declared voltage as stated in PGMD form
Note on D7: Maximum active power at connection point at rated voltage and no reactive power exchange at connection point.
Note on D8: Connection capacity as per connection agreement
Note on C9: Make and type units type 1 as per PGMD form
Note on C10: Make and type units type 2 as per PGMD form
Note on H10: kVA output at terminals of unit with highest kVA output in load flow case
Note on C11: Make and type units type 3 as per PGMD form
Note on H11: voltage at terminals of unit with highest voltage in load flow case
Note on H12: voltage at terminals of unit with lowest voltage in load flow case
Note on D13: Include number and technical data of units type 1
Note on E13: Include number and technical data of units type 2
Note on F13: Include number and technical data of units type 3

## Q-U and Q-P windows park
10.1
-2.8
Load flow cases 6-12: Voltage-Reactive power. Red window needs to cover blue window completely | [8 empty] | Load Flow cases 0-5: Reactive - Active power. Red window needs to cover blue window completely
Uc grid voltage (p.u.) | 1.1 | 1.1 | 1.05 | 0.95 | 0.9 | 0.9 | 0.95 | 1.1 | Uc grid voltage (p.u.) | 1 | 1 | 1 | 1 | 1 | 1 | 1
Active power connection point Pc (MW) | 9.973 | 9.984 | 9.864 | 9.352 | 9.354 | 9.352 | 9.153 | 9.973 | Active power connection point Pc (MW) | -0.007 | 2 | 9.931 | 10.013 | 9.852 | 2 | -0.007
Reactive power connection point Qc (Mvar) | -3.34 | 0.002 | 3.32 | 3.308 | 2.5 | 0 | -3.31 | -3.34 | Reactive power connection point Qc (Mvar) | -0.002 | -3.29 | -3.295 | -0.002 | 3.313 | 3.309 | -0.002
Note on A39: In "Blindvermogen-spanningsvenster" the red and brown window need to cover the blua window for compliance

## Review unit type 1
Load Flow Case | P (Qc=0) | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10 | C11 | C12 | C13 | P3 | P4
Uc grid voltage (p.u.) | 1 | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.05 | 0.95 | 0.95 | 0.9 | 0.9 | 0.85 | 1 | 1
Maximum apparent power unit (p.u.) | 0.94419 | 0.97209 | 1 | 0.35349 | 0.36744 | 0 | 0.97674 | 0.93953 | 1 | 0.95814 | 0.89767 | 0.88372 | 0.91628 | 0.86047 | 0.97209 | 1
Maximum voltage unit (p.u.) | 0.998 | 0.978 | 1.018 | 0.961 | 1.001 | 0.977 | 1.075 | 1.093 | 1.065 | 0.97 | 0.914 | 0.902 | 0.928 | 0.873 | 0.9775 | 1.0175
Minimum voltage unit (p.u.) | 0.987 | 0.968 | 1.004 | 0.96 | 0.997 | 0.977 | 1.066 | 1.083 | 1.052 | 0.956 | 0.901 | 0.889 | 0.919 | 0.86 | 0.9675 | 1.0037
Maximum current unit (p.u.) | 0.95639 | 1.004 | 0.99578 | 0.36813 | 0.36846 | 0 | 0.91605 | 0.86732 | 0.95034 | 1.002 | 0.99607 | 0.99382 | 0.9968 | 1.0003 | 1.0045 | 0.99603
One per unit line | bar: P (Qc=0) to P4

## Review unit type 2
Load Flow Case | P (Qc=0) | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10 | C11 | C12 | C13 | P3 | P4
Uc grid voltage (p.u.) | 1 | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.05 | 0.95 | 0.95 | 0.9 | 0.9 | 0.85 | 1 | 1
Maximum apparent power unit (p.u.) | 0.94419 | 0.97209 | 1 | 0.35349 | 0.36744 | 0 | 0.97674 | 0.93953 | 1 | 0.95814 | 0.89767 | 0.88372 | 0.91628 | 0.86047 | 0.97209 | 1
Maximum voltage unit (p.u.) | 0.998 | 0.978 | 1.018 | 0.961 | 1.001 | 0.977 | 1.075 | 1.093 | 1.065 | 0.97 | 0.914 | 0.902 | 0.928 | 0.873 | 0.9775 | 1.0175
Minimum voltage unit (p.u.) | 0.987 | 0.968 | 1.004 | 0.96 | 0.997 | 0.977 | 1.066 | 1.083 | 1.052 | 0.956 | 0.901 | 0.889 | 0.919 | 0.86 | 0.9675 | 1.0037
Maximum current unit (p.u.) | 0.95639 | 1.004 | 0.99578 | 0.36813 | 0.36846 | 0 | 0.91605 | 0.86732 | 0.95034 | 1.002 | 0.99607 | 0.99382 | 0.9968 | 1.0003 | 1.0045 | 0.99603
One per unit line | bar: P (Qc=0) to P4

## Review unit type 3
Load Flow Case | P (Qc=0) | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10 | C11 | C12 | C13 | P3 | P4
Uc grid voltage (p.u.) | 1 | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.05 | 0.95 | 0.95 | 0.9 | 0.9 | 0.85 | 1 | 1
Maximum apparent power unit (p.u.) | 0.94419 | 0.97209 | 1 | 0.35349 | 0.36744 | 0 | 0.97674 | 0.93953 | 1 | 0.95814 | 0.89767 | 0.88372 | 0.91628 | 0.86047 | 0.97209 | 1
Maximum voltage unit (p.u.) | 0.998 | 0.978 | 1.018 | 0.961 | 1.001 | 0.977 | 1.075 | 1.093 | 1.065 | 0.97 | 0.914 | 0.902 | 0.928 | 0.873 | 0.9775 | 1.0175
Minimum voltage unit (p.u.) | 0.987 | 0.968 | 1.004 | 0.96 | 0.997 | 0.977 | 1.066 | 1.083 | 1.052 | 0.956 | 0.901 | 0.889 | 0.919 | 0.86 | 0.9675 | 1.0037
Maximum current unit (p.u.) | 0.95639 | 1.004 | 0.99578 | 0.36813 | 0.36846 | 0 | 0.91605 | 0.86732 | 0.95034 | 1.002 | 0.99607 | 0.99382 | 0.9968 | 1.0003 | 1.0045 | 0.99603
One per unit line | bar: P (Qc=0) to P4